# Technical Specification for 3-Phase Copper Wound Distribution Transformers 11 or 33 kV/433-250V (Outdoor Type) (250 KVA to 630 KVA)

## SCOPE:

- This specification covers design, engineering, manufacture, assembly, stage testing, inspection and testing before supply and delivery at site of oil immersed, naturally cooled 3-phase 11 kV/433 - 250V and 33kV/433-250V distribution transformers for outdoor use.

- The equipment shall confirm in all respects to high standards of engineering, design and workmanship and shall be capable of performing in continuous commercial operation, in a manner acceptable to the purchaser, who will interpret the meanings of drawings and specification and shall have the power to reject any work or material which, in his judgment is not in accordance therewith. The offered equipment shall be complete with all components necessary for their effective and trouble-free operation. Such components shall be deemed to be within the scope of bidder’s supply irrespective of whether those are specifically brought out in this specification and / or the commercial order or not.

- The transformer and accessories shall be designed to facilitate operation, inspection, maintenance and repairs. The design shall incorporate every precaution and provision for the safety of equipment as well as staff engaged in operation and maintenance of equipment.

- All outdoor apparatus, including bushing insulators with their mountings, shall be designed so as to avoid any accumulation of water.

## STANDARD RATINGS:

The standard ratings shall be 16, 25, 63, 100,160, 200, 250, 315, 400, 500, 630, 1000, 1250, 1600, 2000 and 2500 kVA for 11 kV distribution transformers and 100, 160, 200, 315, 400, 500, 630, 1000, 1250,1600,2000, 2500 kVA for 33 kV distribution transformers.

## STANDARD RATINGS:

  - The major materials used in the transformer shall confirm in all respects to the relevant/specified Indian Standards and international Standards with latest amendments thereof as on bid opening date, unless otherwise specified herein. Some of the applicable Indian Standards are listed as hereunder:

| Indian Standard | Title | International Standards |
| --- | --- | --- |
| IS -2026 | Specification for Power Transformers | IEC 60076-I, 2011 |
| IS1180(Part-I): 2014 IS1180 (Part 2):2019 | Outdoor Type Oil Immersed Distribution Transformers up to and including 2500kVA, 33kV- Specification |  |
| IS 12444 | Specification for Copper wire rod | ASTM B-49 |
| IS-335 | Specification for Transformer/Mineral Oil | BS 148, D-1473, D- 1533-1934 IEC 60296 |
| IS-5 | Specification for colors for ready mixed paints |  |
| IS -104 | Ready mixed paint, brushing zinc chromate, priming |  |
| IS-2099, IS 3347, IS 7421 | Specification for high voltage porcelain bushing | IEC 60137 |
| IS 649 (Part 1 & 2) | Testing for steel sheets and strips and magnetic circuits |  |
| IS- 3024 | Cold rolled grain oriented electrical sheets and strips |  |
| IS – 4257 | Dimensions for clamping arrangements for bushings |  |
| IS – 7421 | Specification for Low Voltage bushings |  |
| IS 3347 (Part 1–3) | Specification for Outdoor Bushings | DIN 42531 / 42532 / 42533 |

| IS - 5484 | Specification for Al. Wire rods | ASTM B – 233 |
| --- | --- | --- |
| IS – 9335 | Specification for Insulating Kraft Paper | IEC 60554 |
| IS - 1576 | Specification for Insulating Press Board | IEC 60641 |
| IS - 6600 | Guide for loading of oil Immersed Transformers | IEC 60076-7 |
| IS - 2362 | Determination of water content in insulating oil |  |
| IS - 6162 | Paper covered Aluminium conductor |  |
| IS - 6160 | Rectangular Electrical conductor for electrical machines |  |
| IS - 5561 | Electrical power connector |  |
| IS – 6103 | Testing of specific resistance of electrical insulating liquids |  |
| IS – 6262 | Method of test for power factor and dielectric constant of electrical insulating liquids |  |
| IS – 6792 | Determination of electrical strength of insulating oil |  |
| IS 10028 (Part 1–3) | Installation and maintenance of transformers |  |

## SERVICE CONDITIONS:

  - The Distribution Transformers to be supplied against this Specification shall be suitable for satisfactory continuous operation under the following climatic conditions as per IS 2026 (Part - I).

- Location	:	At various locations in the country

- Maximum ambient air temperature (0 C)	:	50

- Minimum ambient air temperature (0 C)	:	-5

- Maximum average daily ambient air temperature (0 C)	:	40

- Maximum yearly weighted average ambient temperature(0 C)  :	32

- Maximum altitude above altitude of 5000 mtr mean sea	:	To be specified by the user level (Meters) for HP, J&K, UK, Sikkim, Assam, Meghalaya,

Manipur, Nagaland, Tripura, Arunachal Pradesh and Mizoram.

### Note:

  - The climatic conditions specified above are indicative and can be changed by the user as per requirements.

  - The equipment shall generally be for use in moderately hot and humid tropical climate, conducive to rust and fungus growth unless otherwise specified.

## PRINCIPAL PARAMETERS:

  - The transformers shall be suitable for outdoor installation with three phase, 50 Hz, 11 kV or 33 kV system in which the neutral is effectively earthed and they should be suitable for service with fluctuations in supply voltage up to plus 12.5% to minus 12.5%.

(i)	The transformers shall conform to the following specific parameters:

| Sl. No. | Item | 11 kV Distribution Transformers | 33 kV Distribution Transformers |
| --- | --- | --- | --- |
| 1. | System voltage (Max.) | 12 kV | 36 kV |
| 2. | Rated Voltage (HV) | 11 kV | 33 kV |
| 3. | Rated Voltage (LV) | 433 - 250 V | 433 - 250 V |
| 4. | Frequency | 50 Hz +/- 5% | 50 Hz +/- 5% |
| 5. | No. of Phases | Three | Three |

| 6. | Connection HV | Delta | Delta |
| --- | --- | --- | --- |
| 7. | Connection LV | Star (Neutral brought out) | Star (Neutral brought out) |
| 8. | Vector group | Dyn-11 | Dyn-11 |
| 9. | Type of cooling | ONAN | ONAN |

Audible sound levels (decibels) at rated voltage and frequency for liquid immersed distribution transformers shall be as below (NEMA Standards):

| kVA rating | Audible sound levels (decibels) |
| --- | --- |
| 0-50 | 48 |
| 51-100 | 51 |
| 101-300 | 55 |
| 301-500 | 56 |
| 750 | 57 |
| 1000 | 58 |
| 1500 | 60 |
| 2000 | 61 |
| 2500 | 62 |

### ii)	Minimum guaranteed weight of core, conductor, Transformer oil & minimum thickness of tank sheet shall be as following:

| Sl. No. | Capacity | Minimum Weight of Material |  |  | Minimum Thickness of Tank (mm) |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | KVA | Core (Kg.) | Conductor (Kg.) | Oil (Kg.) | Top & Bottom | Side |
| 1 | 250 | 410 | 240 | 310 | 6 | 4 |
| 2 | 400 | 620 | 390 | 387 | 6 | 4 |
| 3 | 630 | 890 | 489 | 490 | 6 | 4 |

- TECHNICAL REQUIREMENTS:

    - CORE MATERIAL

      - The core shall be stack type of high grade Cold Rolled Grain Oriented steel lamination

having low loss and good grain properties, coated with hot oil proof insulation, bolted together and to the frames firmly to prevent vibration or noise. The core shall be stress relieved by annealing under inert atmosphere if required. The complete design of core must ensure permanency of the core loss with continuous working of the transformers. The value of the maximum flux density allowed in the design and grade of lamination used shall be clearly stated in the offer. Flux density shall not be more than 1.69 Tesla.

      - The bidder should offer the core for inspection and approval by the purchaser during manufacturing stage. CRGO steel for core shall be purchased only from the approved vendors, list of which is available at http://apps.powergridindia.com/ims/ComponentList/Power-former%20upto%20420%20kV-CM%20List.pdf

      - The transformers core shall be suitable for over fluxing (due to combined effect of voltage and frequency) up to 12.5% without injurious heating at full load conditions and shall not get saturated. The bidder shall furnish necessary design data in support of this situation.

      - No-load current up to 200kVA shall not exceed 3% of full load current and will be measured by energizing the transformer at rated voltage and frequency. Increase of 12.5% of rated voltage shall not increase the no-load current by 6% of full load current.

Or

No-load current above 200kVA and up to 2500 kVA shall not exceed 2% of full load current and will be measured by energizing the transformer at rated voltage and frequency. Increase of 12.5% of rated voltage shall not increase the no-load current by 5% of full load current.

      - Please refer to “Check-list for Inspection of Prime quality CRGO for Transformers” attached at Annexure-

        - It is mandatory to follow the procedure given in this Annexure.

      - The name of manufacturer and unique no allotted to him shall also be punched at a visible portion on the core assembly of each transformer.

- WINDINGS:

Material:

    - HV and LV windings shall be wound from Double Paper covered Copper conductor.

    - In HT winding number of Coils per limb should be Minimum 4.

    - LV winding shall be such that neutral formation will be at top.

    - The winding construction of HV coil wound over LV coil is preferable.

    - Inter layer insulation shall be Nomex /Epoxy dotted Kraft Paper.

    - Proper bonding of inter layer insulation with the conductor shall be ensured. Test for bonding strength shall be conducted.

    - Dimensions of winding coils are very critical. Dimensional tolerances for winding coils shall be within limits as specified in Guaranteed Technical Particulars (GTP Schedule I).

    - The core/coil assembly shall be securely held in position to avoid any movement under short circuit conditions.

    - Joints in the winding shall be avoided. However, if joint is necessary the joints shall be properly brazed and the resistance of the joints shall be less than that of parent conductor. In case of foil windings, welding of leads to foil can be done within the winding.

    - Current density for HV and LV winding should not be more than 2.5 Ampere per sq mm for copper and 1.4 Ampere per sq mm for Aluminium Conductor.

- TAPPING RANGES AND METHODS:

No tapping shall be provided for distribution transformers up to 400 KVA. In 630 KVA Tapping Compulsory.

- OIL:

  - The insulating oil shall comply with the requirements of IS 335 or BS 148. Use of recycled oil is not acceptable. The specific resistance of the oil shall not be less than 2.5 x 1012 ohm-cm at 270C when tested as per IS 6103.

  - Oil shall be filtered and tested for break down voltage (BDV) and moisture content before filling.

  - The oil shall be filled under vacuum.

  - The design and all materials and processes used in the manufacture of the transformer, shall be such as to reduce to a minimum the risk of the development of acidity in the oil.

- INSULATION LEVELS:

| Sl. No. | Voltage (kV) | Impulse Voltage (kV Peak) | Power Frequency |
| --- | --- | --- | --- |
| 1. | 0.433 | - | 3 |
| 2. | 11 | 75 | 28 |
| 3. | 33 | 170 | 70 |

- The insulation levels shall be minimum values and shall be tested in accordance with IS 2026. No relaxation shall be permitted without prior approval of the Purchaser.

- LOSSES:

# Table 6 - Maximum Total Losses Up to 11 KV Class Transformers IS:1180(Part-I):2014.

| Sl. No. | Rating KVA | Impedance (%) | Maximum Total Loss (W) Energy Efficiency Previously Level II Now Level I |  |
| --- | --- | --- | --- | --- |
|  |  |  | 50% Load | 100% Load |
| 1 | 250KVA | 4.5 | 980 | 2930 |
| 2 | 400KVA | 4.5 | 1225 | 3450 |
| 3 | 630KVA | 4.5 | 1860 | 5300 |

  - The transformer of HV voltage up to 11kV, the total losses (no-load + load losses at 75 0C) at 50% of rated load and total losses at 100% of rated load shall not exceed the maximum total loss values given in Table-6 above.

  - The maximum permissible losses at rated voltage and rated frequency, measured at 75 °C, for 11/0.433 kV transformers shall be as specified in Table-6 above.

  - The above losses are maximum allowable and there would not be any positive tolerance. Bids with higher losses than the above specified values would be treated as non-responsive. However, the manufacturer can offer losses less than above stated values. The utility can evaluate offers with losses lower than the maximum allowable losses on total owning cost basis in accordance with methodology given in Annex-I.

- TOLERANCES:

No positive tolerance shall be allowed on the maximum losses displayed on the label for both 50% and 100% loading values.

- PERCENTAGE IMPEDANCE:

The percentage impedance of transformers at 75 0C for different ratings up to 200 kVA shall be as per Table 3 and for rating beyond 200 KVA shall be as per table 6 of IS 1180 (Part-I):2014.

- Temperature rise: The temperature rise over ambient shall not exceed the limits given below:

  - The permissible temperature rise limits shall be as per IS 1180, as detailed below:

    - Top oil temperature rise measured by thermometer	:400C

    - Winding temperature rise measured by resistance method	:450C

  - The transformer shall be capable of giving continuous rated output without exceeding the specified temperature rise. Bidder shall submit the calculation sheet in this regard.

- PENALTY FOR NON-PERFORMANCE:

  - During testing at supplier’s works if it is found that the actual measured losses are more than the values quoted by the bidder, the purchaser shall reject the transformer and he shall also have the right to reject the complete lot.

  - Purchaser shall reject the entire lot during the test at supplier’s works, if the temperature rise exceeds the specified values

  - Purchaser shall reject any transformer during the test at supplier’s works, if the impedance values differ from the guaranteed values including tolerance.

## INSULATION MATERIAL:

  - Electrical grade insulation epoxy dotted Kraft Paper/Nomex and press board of standard make or any other superior material subject to approval of the purchaser shall be used.

  - All spacers, axial wedges / runners used in windings shall be made of pre-compressed Press board- solid, conforming to type B 3.1 of IEC 641-3-2. In case of cross-over coil winding of HV all spacer shall be properly sheared and dovetail punched to ensure proper locking. All axial wedges / runners shall be properly milled to dovetail shape so that they pass through the designed spacers freely. Insulation shearing, cutting, milling, and punching operations shall be carried out in such a manner that no burrs, surface damage, or dimensional variations are present.

  - TANK:

    - Transformer tank construction shall conform in all respect to clause 15 of IS 1180(Part-1):2014.

    - The internal clearance of tank shall be such, that it shall facilitate easy lifting of core with coils from the tank without dismantling LV bushings.

    - All joints of tank and fittings shall be oil tight and no bulging should occur during service.

    - Inside of tank shall be painted with varnish/hot oil resistant paint.

    - The top cover of the tank shall be slightly sloping to drain rain water.

    - The tank plate and the lifting lugs shall be of such strength that the complete transformer filled with oil may be lifted by means of lifting shackle/Hook type.

    - Manufacturer should carry out all welding operations as per the relevant ASME standards and submit a copy of the welding procedure and welder performance qualification certificates to the customer.

  - PLAIN TANK:

    - The transformer tank shall be of robust construction rectangular/octagonal/round/ elliptical in shape and shall be built up of electrically tested welded mild steel plates of thickness of 3.15 mm for the bottom and top and not less than 2.5 mm for the sides for distribution transformers up to 16 kVA, 5.0 mm and

3.15mm respectively for transformers from 25KVA up to and including 100 kVA and 6 mm and 4mm respectively above 100 kVA. Tolerances as per IS1852 shall be applicable.

    - In case of rectangular tanks above 100 kVA the corners shall be fully welded at the corners from inside and outside of the tank to withstand a pressure of 0.8 kg/cm2 for 30 minutes. In case of transformers of 100 kVA and below, there shall be no joints at corners and there shall not be more than 2 joints in total.

    - Under operating conditions the pressure generated inside the tank should not exceed 0.4 kg/ sq. cm positive or negative. There must be sufficient space from the core to the top cover to take care of oil expansion. The space above oil level in the tank shall be filled with dry air or nitrogen conforming to commercial grade of IS 1747.

- The tank shall be reinforced by welded flats on all the outside walls on the edge of the tank.

- Permanent deflection: The permanent deflection, when the tank without oil is subjected to a vacuum of 525mm of mercury for rectangular tank and 760 mm of mercury for round tank, shall not be more than the values as given below. (All figures are in mm).

| Horizontal length of flat plate | Permanent deflection |
| --- | --- |
| Up to and including 750 | 5.0 |
| 751 to 1250 | 6.5 |
| 1251 to 1750 | 8.0 |
| 1751 to 2000 | 9.0 |

    - The tank shall further be capable of withstanding a pressure of 0.8kg/sq.cm and a vacuum of 0.7 kg/sq.cm (g) without any deformation.

    - The radiators can be tube type or fin type or pressed steel type to achieve the desired cooling to limit the specified temperature rise.

  - CORRUGATED TANK:

    - The bidder may offer corrugated tanks for transformers of all ratings.

    - The transformer tank shall be of robust construction corrugated in shape and shall be built up of tested sheets.

    - Corrugation panel shall be used for cooling. The transformer shall be capable of giving continuous rated output without exceeding the specified temperature rise. Bidder shall submit the calculation sheet in this regard.

    - Tanks with corrugations shall be tested for leakage test at a pressure of 0.25kg/ sq cm measured at the top of the tank.

    - The transformers with corrugation should be provided with a pallet for transportation, the dimensions of which should be more than the length and width of the transformer tank with corrugations.

- CONSERVATOR:

- Transformers of rating 63 kVA and above with plain tank construction, the provision of conservator is mandatory. For corrugated tank and sealed type transformers with or without inert gas cushion, conservator is not required.

- When a conservator is provided, oil gauge and the plain or dehydrating breathing device shall be fitted to the conservator which shall also be provided with a drain plug and a filling hole [32 mm(1¼”)] normal size thread with cover. In addition, the cover of the main tank shall be provided with an air release plug.

- The dehydrating agent shall be silica gel. The moisture absorption shall be indicated by a change in the colour of the silica gel crystals which should be easily visible from a distance. Volume of breather shall be suitable for 500g of silica gel conforming to IS 3401 for transformers up to 200 kVA and 1 kg for transformers above 200 kVA.

- The capacity of a conservator tank shall be designed keeping in view the total quantity of oil and its contraction and expansion due to temperature variations. The total volume of conservator shall be such as to contain 10% quantity of the oil. Normally 3% quantity the oil shall be contained in the conservator.

- The cover of main tank shall be provided with an air release plug to enable air trapped within to be released, unless the conservator is so located as to eliminate the possibility of air being trapped within the main tank.

- The inside diameter of the pipe connecting the conservator to the main tank should be within 20mm to 50 mm and it should be projected into the conservator so that its end is approximately 20 mm above the bottom of the conservator so as to create a sump for collection of impurities. The minimum oil level (corresponding to -50C) should be above the sump level.

## SURFACE PREPARATION AND PAINTING:

  - GENERAL:

    - All paints, when applied in a normal full coat, shall be free from runs, sags, wrinkles, patchiness, brush marks or other defects.

    - All primers shall be well marked into the surface, particularly in areas where painting is evident and the first priming coat shall be applied as soon as possible after cleaning. The paint shall be applied by airless spray according to manufacturer’s recommendations. However, where ever airless spray is not possible, conventional spray be used with prior approval of purchaser.

  - CLEANING AND SURFACE PREPARATION:

    - After all machining, forming and welding has been completed, all steel work surfaces shall be thoroughly cleaned of rust, scale, welding slag or spatter and other contamination prior to any painting.

    - Steel surfaces shall be prepared by shot blast cleaning (IS9954) to grade Sq.2.5 of ISO 8501-1 or chemical cleaning including phosphating of the appropriate quality (IS 3618).

    - Chipping, scraping and steel wire brushing using manual or power-driven tools cannot remove firmly adherent mill-scale. These methods shall only be used where blast cleaning is impractical. Manufacturer to clearly explain such areas in his technical offer.

  - PROTECTIVE COATING:

    - As soon as all items have been cleaned and within four hours of the subsequent drying, they shall be given suitable anti-corrosion protection.

  - PAINT MATERIAL:

- Following are the types of paint which may be suitably used for the items to be painted at shop and supply of matching paint to site:

Heat resistant paint (Hot oil proof) for inside surface

- For external surfaces one coat of thermosetting powder paint or one coat of epoxy primer followed by two coats of synthetic enamel/ polyurethane base paint. These paints can be either air drying or stoving.

- For highly polluted areas, chemical atmosphere or for places very near to the sea coast, paint as above with one coat of high build Micaceous iron oxide (MIO) as an intermediate coat may be used.

  - PAINTING PROCEDURE:

- All prepared steel surfaces should be primed before visible re-rusting occurs or within 4 hours, whichever is sooner. Chemical treated steel surfaces shall be primed as soon as the surface is dry and while the surface is still warm.

- Where the quality of film is impaired by excess film thickness (wrinkling, mud cracking or general softness) the supplier shall remove the unsatisfactory paint coating and apply another coating. As a general rule, dry film thickness should not exceed the specified minimum dry film thickens by more than 25%.

  - DAMAGED PAINT WORK:

- Any damage occurring to any part of a painting scheme shall be made good to the same standard of corrosion protection and appearance as that was originally applied.

- Any damaged paint work shall be made good as follows:

    - The damaged area, together with an area extending 25 mm around its boundary, shall be cleaned down to bare metal.

    - A priming coat shall be immediately applied, followed by a full paint finish equal to that originally applied and extending 50 mm around the perimeter of the original damage.

    - The repainted surface shall present a smooth surface. This shall be obtained by carefully chamfering the paint edges before and after priming.

  - DRY FILM THICKNESS:

    - To the maximum extent practicable the coats shall be applied as a continuous film of uniform thickness and free of pores. Overspray, skips, runs, sags and drips should be avoided. The different coats may or may not be of the same colour.

    - Each coat of paint shall be allowed to harden before the next is applied as per manufacturer’s recommendation.

    - Particular attention must be paid to full film thickness at the edges.

    - The requirements for the dry film thickness (DFT) of paint and the materials to be used shall be as given below:

| Sl. No. | Paint type | Area to be painted | No. of coats | Total dry film thickness (min.) (microns) |
| --- | --- | --- | --- | --- |
| 1. | Thermo setting powder paint | inside outside | 01 01 | 30 60 |
| 2. | Liquid paint - Epoxy (primer) - P.U. Paint(Finish coat) - Hot oil paint/ Varnish | outside outside inside | 01 02 01 | 30 25 each 35/10 |

## TESTS FOR PAINTED SURFACE:

    - The painted surface shall be tested for paint thickness.

    - The painted surface shall pass the cross hatch adhesion test and impact test as acceptance tests and Salt spray test and Hardness test as type test as per the relevant ASTM standards.

Note: Supplier shall guarantee the painting performance requirement for a period of not less than 5 years.

## BUSHINGS:

  - The bushings shall conform to the relevant standards specified and shall be of outdoor type. The bushing rods and nuts shall be made of brass material 12 mm diameter for both HT and LT bushings. The bushings shall be fixed to the transformers on side with straight pockets and in the same plane or the top cover for transformers above 100 kVA. For transformers of 100 kVA and below the bushing can be mounted on pipes. The tests as per latest IS 2099 and IS 7421 shall be conducted on the transformer bushings.

  - For 33 kV - 36 kV class bushings, for 11 kV - 12 kV class bushings and for 0.433 kV - 1 kV class bushings shall be used.

  - Bushing can be of porcelain/epoxy material. Polymer insulator bushings conforming with relevant IEC can also be used.

  - Bushings of plain shades as per IS 3347 shall be mounted on the side of the Tank and not on top cover.

  - Dimensions of the bushings of the voltage class shall conform to the Standards specified and dimension of clamping arrangement shall be as per IS 4257

  - Minimum external phase to phase and phase to earth clearances of bushing terminals shall be as follows:

| Voltage | Clearance |  |
| --- | --- | --- |
|  | Phase to phase | Phase to earth |
| 33 kV | 350mm | 320mm |
| 11 kV | 255mm | 140mm |
| LV | 75mm | 40mm |

For DTs of 200 KVA and above, the clearances of cable box shall be as below:

| Voltage | Clearance |  |
| --- | --- | --- |
|  | Phase to phase | Phase to earth |
| 33 kV | 350mm | 220mm |
| 11 kV | 130mm | 80mm |
| LV | 25mm | 20mm |

  - Lighting arrestors shall be provided on HV bushing.

  - Brazing of all inter connections, jumpers from winding to bushing shall have cross section larger than the winding conductor. All the Brazes shall be qualified as per ASME, section – IX.

  - The bushings shall be of reputed make supplied by those manufacturers who are having manufacturing and testing facilities for insulators.

  - The terminal arrangement shall not require a separate oil chamber not connected to oil in the main tank.

- TERMINAL CONNECTORS:

  - The LV and HV bushing stems shall be provided with suitable terminal connectors as per IS 5082 so as to connect the jumper without disturbing the bushing stem. Connectors shall be with eye bolts so as to receive conductor for HV. Terminal connectors shall be type tested as per IS 5561.

- LIGHTNING ARRESTORS:

9 kV, 5 kA metal oxide lightning arrestors Distribution class type of reputed make as per relevant standard, one number per phase shall be provided to be fitted under the HV bushing with GI earth strip 25×4 mm connected to the body of the transformer with necessary clamping arrangement. The lightning arrester with polymer insulator, in confirmation to the relevant IS, can also be used.

- CABLE BOXES:

  - Only for DT below 200 KVA. For DTs above 200 KVA rating cable box only on LV side will be provided for MCCB.

- TERMINAL MARKINGS:

High voltage phase windings shall be marked both in the terminal boards inside the tank and on the outside with capital letter 1U, 1V, 1W and low voltage winding for the same phase marked by corresponding letter 2U, 2V, 2W. The neutral point terminal shall be indicated by the letter 2N. Neutral terminal is to be brought out and connected to local grounding terminal by an earthing strip.

- THE FOLLOWING STANDARD FITTINGS SHALL BE PROVIDED:

- Rating and terminal marking plates, non-detachable.

- Earthing terminals with lugs - 2 Nos.

- Lifting lugs for main tank and top cover

- Terminal connectors on the HV/LV bushings (For bare terminations only).

- Thermometer pocket with cap - 1 No.

- Air release device (for non-sealed transformer)

- HV bushings - 3 Nos.

- LV bushings - 4 Nos.

- Pulling lugs.

- Stiffener

- Radiators - No. and length may be mentioned (as per heat dissipation calculations)/ corrugations.

- Lighting Arrestor 9kV, 5 KA.

- Prismatic oil level gauge.

- One filter valve on upper side of the transformer (for transformer above 200 kVA)

- Oil filling hole having 1¼″ BSP threaded connection, complete with a threaded plug. A drain plug shall also be provided on the conservator.

- Silica gel breather (for non-sealed transformer)

- Base channel 75x40 mm for up to 100 kVA and 100 mmx50 mm above 100 kVA, 460 mm long with holes to make them suitable for fixing on a platform or plinth.

- 4 No. rollers for transformers of 200 kVA and above.

- Pressure relief device or explosion vent (above 200 kVA).

- Oil level gauge

- -5 deg. Celsius and 90 Deg. Celsius marking for non-sealed type transformer,

- 30 Deg. Celsius marking for non-sealed type transformer,

- No drain valve needed transformer up to 100 KVA.

- FASTENERS:

  - All bolts, studs, screw threads, pipe threads, bolt heads and nuts shall comply with the appropriate Indian Standards for metric threads, or the technical equivalent.

  - Bolts or studs shall not be less than 6 mm in diameter except when used for small wiring terminals.

  - All nuts and pins shall be adequately locked.

  - Wherever possible bolts shall be fitted in such a manner that in the event of failure of locking resulting in the nuts working loose and falling off, the bolt will remain in position.

  - All bolts/nuts/washers exposed to atmosphere should be follows,

- Size 12 mm or below - stainless steel,

- Above 12 mm - steel with suitable finish like electro galvanized with passivation or hot dip galvanized.

  - Each bolt or stud shall project at least one thread but not more than three threads through the nut, except when otherwise approved for terminal board studs or relay stems. If bolts and nuts are placed so that they are inaccessible by means of ordinary spanners, special spanners shall be provided.

  - The length of the screwed portion of the bolts shall be such that no screw thread may form part of a shear plane between members.

  - Taper washers shall be provided where necessary.

  - Protective washers of suitable material shall be provided front and back of the securing screws.

- OVERLOAD CAPACITY:

  - The transformers shall be suitable for loading as per IS 6600.

#### TESTS and PENALTIES:

This shall be asper UPPCL Letter No. I/29203/2025/RESSPO/Quality Cell/Sampling Dated – 29/10/2025

### Procedure for Sample Selection from the supplied DI:

### If Di quantity is more than 300: 2 Samples will be selected from the DI by UQC

### If Di quantity is less than 300: 1 Sample will be selected from the DI by UQC

### If multiple DIs are created against single Pre-dispatch Inspection, UQC will club together one or more such DIs to select 1 or 2 final samples based on total inspected quantity as per criteria given in 1(a) and 1(b). UQC will ensure that unnecessary samples are not selected from multiple DIs of single inspected lot.

### Procedure for Sample Sealing:

Sample will be sealed in accordance with the provisions of UPPCL order no. 837/Resspo/QC, dated 18.05.2024.

### Dispatch of Selected Sample:

Sealed Samples will be dispatched in accordance with the provisions of UPPCL order no. 837/Resspo/QC, dated 18.05.2024.

### Tests to be conducted on Selected Sample:

- The sample of distribution transformer will be tested for following routine tests:

  - Measurement of winding resistance [IS 2026 (Part-1)]

  - Measurement of voltage ratio and check of phase displacement [IS 2026 (Part-1)]

  - Measurement of Short Circuit Impedance and Load Loss at 50 percent and 100 percent load [IS 2026 (Part-1)]

  - Measurement of No-load loss and current [IS 2026 (Part-1)]

  - Measurement of Insulation resistance [IS 2026 (Part 1)]

  - Induced over voltage withstand test [IS 2026 (Part 3)]

  - Separate source voltage withstand test (IS 2026 (Part-3)]

  - Oil leakage test [IS 1180 (Part-1): 2024)]

  - Temperature Rise Test [IS 2026 (rt-2)]

- Tests to be performed on D.T. sample are given below:

  - Measurement of No-load loss and current [IS 2026 (Part-1)]

  - Measurement of Short Circuit Impedance and load loss at 50% and 100% load [IS 2026 (Part-1)]

  - Temperature Rise Test

  - Measurement of Voltage Ration and check of phase displacement [IS 2026 (Part-1)]

  - Measurement of winding resistance [IS 2026 (Part-1)]

  - Measurement of Insulation resistance [IS 2026 (Part-1)]

  - Induced over voltage withstand test [IS 2026 (Part-3)]

  - Separate source voltage withstand test [IS 2026 (Part-3)]

  - Oil leakage test [IS 1180 (Part-1): 20141

- Although the regular samples selected will be subjected to routine tests listed above in Point 28.4 (a), U.P.P.C.L., through U.Q.C. (UPPCL Quality Cell), reserves its rights to conduct any or all of the following Type Tests at any or all of the randomly selected samples or fresh samples:

  - Lightning Impulse Test

  - Short Circuit Withstand Test

  - Pressure Test

UQC will mark any sample for above Type Tests after the approval of Chairman, UPPCL.

- The results of all the tests enumerated in 28.4 (a) and 28.4 (b) will be binding on the suppliers and the DISCOMS.

- DQC shall coordinate with the test labs to ensure that the tests enlisted above are conducted on sample as soon as possible. However, even if test lab takes time, the supplier will be liable to Penal Provisions given in Point-28.4.1 as below, irrespective of the time incurred in testing, if the sample is found non-conforming in any test.

28.4.1 Action to be taken against suppliers, in case a sample is found non-conforming to the above test parameters:

    - If the material of whole lot has not been utilized, following penal actions will be taken on the supplier to ensure good quality supply:

| Case | Failure | Penal Action |  |  |
| --- | --- | --- | --- | --- |
|  |  | Replacement | Financial Penalty | Debarment/Blacklisting |
| Failure 1 | -First time failure in supply of lot | 100% | Nil | Nil |
| Failure-2 | Second time Failure in subsequent lot or replaced previous lots of the same P. Ο. | 100% | 10% of ex-works (including F and 1) value of the lot | Nil |
| Failure-3 | Third time Failure in subsequent lot or replaced previous lots of the same P.Ο. | 100% | Encashment of performance bank guarantee | Debarment/Blacklisting from business in all DISCOMs for 2 years |

    - If the material of each lot has been utilized due to urgent/necessary requirement, following penal actions will be taken on the supplier:

| Failure | Penal Action |  |
| --- | --- | --- |
|  | Financial Penalty | Debarment/Blacklisting |
| Failure of sample in any test listed in 28.4(a) but passed in Losses Test (Load Loss Test at 50% and 100% Load) | 20% of ex-works (including F and I) value of the lot | Nil |
| Failure of sample in Test(s) including Losses Test (Load Loss test at 50% and 100% Load). | 20% of ex-works (including F and I) value of the lot and encashment of performance bank guarantee | Debarment/Blacklisting from business in all DISCOMs for 2 years |
| Failure of sample in any test listed in 28.4(c) | 20% of ex-works (including F and I) value of the lot and encashment of performance bank guarantee | Debarment/Blacklisting from business in all DISCOMs for 2 years |

    - The provisions in the above tables mentioned in point-

- and (b) as above shall be implemented in the following order:

  - If the whole lot is completely unutilized till the receipt of the test reports, Table in (a) will be applicable.

  - If the whole lot is completely utilized till the receipt of the test reports, Table in (b) will be applicable.

  - If the lot is partially utilized till the receipt of the test reports, table in (b) will be applicable on utilized portion of lot whereas table in (a) will be applicable on unutilized portion of lot.

All the equipment offered shall be fully type tested by the bidder or his collaborator as per the relevant standards including the additional type tests. The type test must have been conducted on a transformer of same design during the last five years at the time of bidding. The bidder shall furnish four sets of type test reports along with the offer. Offer without type test reports will be treated as non- responsive. In case report from CPRI/ERDA/NTH are not available at the time of bidding firm shall furnish at the time of stage inspection (A scheduled undertaking is required). All financial liability of conducting type test shall be of bidders.

### Special tests other than type and routine tests, as agreed between purchaser and bidder shall also be carried out as per the relevant standards.

### The test certificates for all routine and type tests for the transformers and also for the bushings and transformer oil shall be submitted after the receipt of order.

### The procedure for testing shall be in accordance with IS1180 (Part-1) :2014 /2026 as the case may be except for temperature rise test.

### Before dispatch each of the completely assembled transformers shall be subjected to the routine tests at the manufacturer’s works.

#### ROUTINE TESTS:

  - Ratio, polarity, phase sequence and vector group.

  - No Load current and losses at service voltage and normal frequency.

  - Load losses at rated current and normal frequency.

  - Impedance voltage test.

  - Resistance of windings at each tap, cold (at or near the test bed temperature).

  - Insulation resistance.

  - Induced over voltage withstand test.

  - Separate source voltage withstand test.

  - Neutral current measurement-The value of zero sequence current in the neutral of the star winding shall not be more than 2% of the full load current.

  - Oil samples (one sample per lot) to comply with IS 1866.

  - Measurement of No-load losses and magnetizing current at rated frequency and 90%, 100% and 110% rated voltage.

  - Pressure and vacuum test for checking the deflection on one transformer of each type in every inspection.

#### TYPE TESTS TO BE CONDUCTED ON ONE UNIT:

- In addition to the tests mentioned in clause 31 and 32 following tests shall be conducted:

- Temperature rise test for determining the maximum temperature rise after continuous full load run. The ambient temperature and time of test should be stated in the test certificate.

- Impulse voltage test: with chopped wave of IS 2026 part-III. BIL for 11 kV shall be 75 kV peak(min).

- Short circuit withstand test: Thermal and dynamic ability.

- Air Pressure Test: As per IS – 1180 (Part-1):2014.

- Magnetic Balance Test.

- Un-balanced current test: The value of unbalanced current indicated by the ammeter shall not be more than 2% of the full load current.

- Noise-level measurement.

- Measurement of zero-phase sequence impedance.

- Measurement of Harmonics of no-load current. Transformer tank shall be subjected to specified vacuum. The tank designed for vacuum shall be tested at an internal pressure of 0.35 kg per sq cm absolute (250 mm of Hg) for one hour. The permanent deflection of flat plates after the vacuum has been released shall not exceed the values specified below:

| Horizontal length of flat plate (in mm) | Permanent deflection (in mm) |
| --- | --- |
| Up to and including 750 | 5.0 |
| 751 to 1250 | 6.5 |
| 1251 to 1750 | 8.0 |
| 1751 to 2000 | 9.0 |

- Transformer tank together with its radiator and other fittings shall be subjected to pressure corresponding to twice the normal pressure or 0.35 kg / sq.cm whichever is lower, measured at the base of the tank and maintained for an hour. The permanent deflection of the flat plates after the excess pressure has been released, shall not exceed the figures for vacuum test.

- Pressure relief device test: The pressure relief device shall be subject to increasing fluid pressure. It shall operate before reaching the test pressure as specified in the above class. The operating pressure shall be recorded. The device shall seal-off after the excess pressure has been released.

- Short Circuit Test and Impulse Voltage Withstand Tests: The purchaser intends to procure transformers designed and successfully tested for short circuit and impulse test. In case the transformers proposed for supply against the order are not exactly as per the tested design, the supplier shall be required to carry out the short circuit test and impulse voltage withstand test at their own cost in the presence of the representative of the purchaser.

- The supply shall be accepted only after such test is done successfully, as it confirms on successful with stand of short circuit and healthiness of the active parts thereafter on un-tanking after a short circuit test.

- Apart from dynamic ability test, the transformers shall also be required to withstand thermal ability test or thermal withstand ability will have to be established by way of calculations.

- It may also be noted that the purchaser reserves the right to conduct short circuit test and impulse voltage withstand test in accordance with the IS, afresh on each ordered rating at purchaser cost, even if the transformers of the same rating and similar design are already tested. This test shall be carried out on at Transformer to be selected by the purchaser either at the manufacturer’s works when they are offered in a lot for supply or randomly from the supplies already made to purchaser’s stores. The findings and conclusions of these tests shall be binding on the supplier.

- Type test certificates for the tests carried out on prototype of same specifications shall be submitted along with the bid. The purchaser may select the transformer for type tests randomly.

#### ACCEPTANCE TESTS:

- At least 10% transformers of the offered lot (minimum of one) shall be subjected to the following routine/acceptance test in presence of purchaser’s representative at the place of manufacture before dispatch without any extra charges. The testing shall be carried out in accordance with IS:1180 (Part-1): 2014 and IS:2026.

- Checking of weights, dimensions, fitting and accessories, tank sheet thickness, oil quality, material, finish and workmanship as per GTP and contract drawings on one transformer on each type in every inspection.

- Physical verification of core coil assembly and measurement of flux density of one unit of each rating, in every inspection with reference to short circuit test report.

- Temperature rise test on one unit of the total ordered quantity.

#### TESTS AT SITE:

The purchaser will conduct the following test on receipt of transformer in their store. The utility shall be arranged all equipment tools & tackle and man power for the testing. All such test shall be conducted by utility not later than 10 days from the receipt of transformer.

- Megger test

- Ratio Test

#### INSPECTION:

  - In respect of raw material such as core stampings, winding conductors, insulating paper and oil, supplier shall use materials manufactured/supplied by standard manufacturers and furnish the manufacturers’ test certificate as well as the proof of purchase from these manufacturers (excise gate pass) for information of the purchaser. The bidder shall furnish following documents along with their offer in respect of the raw materials:

- Invoice of supplier.

- Mill’s certificate.

- Packing list.

- Bill of landing.

- Bill of entry certificate by custom.

Please refer to “Check-list for Inspection of Prime quality CRGO for Transformers” attached at Annexure-A. It is mandatory to follow the procedure given in this Annexure.

#### INSPECTION AND TESTING OF TRANSFORMER OIL:

- To ascertain the quality of the transformer oil, the original manufacturer's tests report should be submitted at the time of inspection. Arrangements should also be made for testing of transformer oil as per IS: 335, after taking out the sample from the manufactured transformers and tested in the presence of purchaser’s representative.

- To ensure about the quality of transformers, the inspection shall be carried out by the purchaser’s representative at following two stages: -

    - Anytime during receipt of raw material and manufacture/ assembly whenever the purchaser desires.

    - At finished stage i.e. transformers are fully assembled and are ready for dispatch.

- The stage inspection shall be carried out in accordance with Annexure-II.

- After the main raw-material i.e. core and coil material and tanks are arranged and transformers are taken for production on shop floor and a few assemblies have been completed, the firm shall intimate the purchaser in this regard, so that an officer for carrying out such inspection could be deputed, as far as possible within seven days from the date of intimation. During the stage inspection a few assembled cores shall be dismantled to ensure that the laminations used are of good quality. Further, as and when the transformers are ready for dispatch, an offer intimating about the readiness of transformers, for final inspection for carrying out tests as per relevant IS shall be sent by the firm along with Routine Test Certificates. The inspection shall normally be arranged by the purchaser at the earliest after receipt of offer for pre-delivery inspection. The proforma for pre delivery inspection of Distribution transformers is placed at Annex- III.

- In case of any defect/defective workmanship observed at any stage by the purchaser’s Inspecting Officer, the same shall be pointed out to the firm in writing for taking remedial measures. Further processing should only be done after clearance from the Inspecting Officer/ purchaser.

- All tests and inspection shall be carried out at the place of manufacture unless otherwise specifically agreed upon by the manufacturer and purchaser at the time of purchase. The manufacturer shall offer the Inspector representing the Purchaser all reasonable facilities, without charges, to satisfy him that the material is being supplied in accordance with this specification. This will include Stage Inspection during manufacturing stage as well as Active Part Inspection during Acceptance Tests.

- The manufacturer shall provide all services to establish and maintain quality of workman ship in his works and that of his sub-contractors to ensure the mechanical /electrical performance of components, compliance with drawings, identification and acceptability of all materials, parts and equipment as per latest quality standards of ISO 9000.

- Purchaser shall have every right to appoint a third-party inspection to carry out the inspection process.

- The purchaser has the right to have the test carried out at his own cost by an independent agency wherever there is a dispute regarding the quality supplied. Purchaser has right to test 1% of the supply selected either from the stores or field to check the quality of the product. In case of any deviation purchaser have every right to reject the entire lot or penalize the manufacturer, which may lead to blacklisting, among other things.

#### QUALITY ASSURANCE PLAN:

- The bidder shall invariably furnish following information along with his bid, failing which his bid shall be liable for rejection. Information shall be separately given for individual type of equipment offered.

- Statement giving list of important raw materials, names of sub-suppliers for the raw materials, list of standards according to which the raw materials are tested, list of tests normally carried out on raw materials in the presence of bidder’s representative, copies of test certificates.

- Information and copies of test certificates as above in respect of bought out accessories.

- List of manufacturing facilities available.

- Level of automation achieved and list of areas where manual processing exists.

- List of areas in manufacturing process, where stage inspections are normally carried out for   and details of such tests and inspection.

- List of testing equipment available with the bidder for final testing of equipment along with valid calibration reports. These shall be furnished with the bid. Manufacturer shall possess 0.1 accuracy class instruments for measurement of losses.

- Quality Assurance Plan (QAP) withhold points for purchaser’s inspection.

- The successful bidder shall within 30 days of placement of order, submit following information to the purchaser:

    - List of raw materials as well as bought out accessories and the names of sub-suppliers selected from those furnished along with offer.

    - Type test certificates of the raw materials and bought out accessories.

    - The successful bidder shall submit the routine test certificates of bought out accessories and central excise passes for raw material at the time of routine testing.

    - ISI Marking on the transformer is mandatory. As per quality control order for electrical transformer- 2015, issued by department of Heavy Industries, the standard/ISI marking on the distribution transformer is mandatory and the product should be manufactured in compliance with IS 1180 part-1(2014).

  - DOCUMENTATION:

  - The bidder shall furnish along with the bid the dimensional drawings of the items offered indicating all the fittings.

  - Dimensional tolerances.

  - Weight of individual components and total weight.

  - An outline drawing front (both primary and secondary sides) and end-elevation and plan of the tank and terminal gear, wherein the principal dimensions shall be given.

  - Typical general arrangement drawings of the windings with the details of the insulation ateach point and core construction of transformer.

  - Typical general arrangement drawing showing both primary and secondary sides and end-elevation and plan of the transformer.

  - PACKING AND FORWARDING:

  - The packing shall be done as per the manufacturer’s standard practice. However, it should be ensured that the packing is such that, the material would not get damaged during transit by Rail / Road / Sea.

  - The marking on each package shall be as per the relevant IS.

- GUARANTEE:

The material will be guaranteed for a period of at least 120 calendar months from the date of installation at the site or 132 months from the date of receipt of material by the purchaser at the site/store, whichever is earlier, called the "maintenance period." If the material is damaged within the guarantee period, it shall be replaced/repaired by the supplier free of cost within one month of receipt of intimation.

If a transformer is damaged within above guarantee period, then the guarantee period of the repaired transformer will be extended by 12 months. The total guarantee period will now be 132/144 months as applicable."

Both stage and final inspection of at least 30-50 percent of the quantity of repaired transformer will be carried out at the manufacturer's works/local repairing center. The manufacturer has to inform the address of the local repairer in advance.

In case, the repair work/replacement of transformer is not affected within three months of the above notice/intimation the consignees will ensure deduction of the amount equal to the price of new transformer from pending bills of the contractor. Such defaults shall be taken into consideration by the consignees while evaluating and reporting the performance of the contractor.

The outage period i.e., period form the date of failure till unit is repaired/replaced shall not be counted for arriving at the guarantee period.

In the event of the supplier’s inability to adhere to the aforesaid provisions, suitable penal action will be taken against the supplier which may inter alia include blacklisting of the firm for future business with the purchaser for a certain period.

Further, installation of 20 percent Distribution Transformers (both new and repaired) shall be carried out in the supervision of manufacturer’s representative.

In the case of award of trial purchase order, the material will be guaranteed for a period of at least 144 calendar months from the date of installation at the site or 156 months from the date of receipt of material by the purchaser at the site/store, whichever is earlier, called the "maintenance period." If the material is damaged within the guarantee period, it shall be replaced/repaired by the supplier free of cost within one month of receipt of intimation.

- SCHEDULES:

  - The bidder shall fill in the following schedule which will be part of the offer. If the schedule are not submitted duly filled in with the offer, the offer shall be liable for rejection.

Schedule-A: Guaranteed Technical Particulars Schedule-B: Schedule of Deviations

- DEVIATIONS:

  - The bidders are not allowed to deviate from the principal requirements of the Specifications. However, the bidder is required to submit with his bid in the relevant schedule a detailed list of all deviations without any ambiguity. In the absence of a deviation list in the deviation schedules, it is understood that such bid conforms to the bid specifications and no post-bid negotiations shall take place in this regard.

  - The discrepancies, if any, between the specification and the catalogues and / or literatures submitted aspart of the offer by the bidders, shall not be considered and representations in this regard shall not be entertained.

  - If it is observed that there are deviations in the offer in guaranteed technical particulars other than those specified in the deviation schedules then such deviations shall be treated as deviations.

  - All the schedules shall be prepared by vendor and are to be enclosed with the bid.

#### Annex-I METHODOLOGY FOR COMPUTING TOTAL OWNING COST

| TOC = IC + (A xWi) + (B xWc) ; Losses in KW |  |  |
| --- | --- | --- |
| Where, |  |  |
| TOC | = | Total Owning Cost |
| IC | = | Initial cost including taxes of transformer as quoted by the manufacturer |
| A factor | = | Cost of no load losses in Rs/KW (A = 288239) |
| B factor | = | Cost of load losses in Rs/KW (B = 93678) |
| Wi | = | No load losses quoted by the manufacturer in KW |
| Wc | = | Load losses quoted by the manufacturer in KW |

If any manufacturer want to add the "Better Operations & Life by Analytics (BOLA) system" with the transformer, it may be acceptable. But it is optional. Specification of BOLA is attached with this tender.

***************