MEDCO/3087/2026

Annexure II

PROFORMA FOR STAGE INSPECTION OF DISTRIBUTION TRANSFORMERS

(A) GENERAL INFORMATION:

1. Name of firm : M/s.

2. Order No. and Date :

3. Rating-wise quantity offered :

4. Details of offer

a) Rating

b) Quantity

c) Serial Numbers

5. Details of last stage inspected lot:

a) Total quantity inspected

b) Serial Numbers

c) Date of stage inspection

d) Quantity offered for final

inspection of

(a) above with date

(B) Availability of material for offered quantity :

Details to be filled in

(C) Position of manufacturing stage of the offered quantity :

a) Complete tanked assembly

b) Core and coil assembly ready

c) Core assembled

d) Coils ready for assembly

(i) HV Coils

(ii) LV Coils

Note: (i) A quantity of less than 100 Nos. shall not be entertained for stage inspection.

If awarded quantity is less than 100 nos. than whole lot shall be offered in single lot.

(ii) The stage inspection shall be carried out in case :-

(a) At least 25% quantity offered has been tanked and

(b) core coil assembly of further at least 30% of the quantity offered has been

completed.

(iii) Quantity offered for stage inspection should be offered for final Inspection within 15 days from the

date of issuance of clearance for stage inspection, otherwise stage inspection already cleared shall

be liable for cancellation.

Sl. Particulars As offered As observed Deviation and

No Remarks

(D) Inspection of Core:

(I) Core Material

(1) Manufacturer’s Characteristic

Certificate in respect of grade of

lamination used. (Please furnish

test certificate)

(2) Remarks regarding Rusting

and smoothness of core.

(3) Whether laminations used for

top and bottom yoke are in one

piece.

(II) Core Construction :

(1) No. of Steps

(2) Dimension of Steps

Step No. 1 2 3 4 5 6 7 8  9 10 11  12

As offered:

W mm

T mm

As found:

W mm

T mm

(3) Core Dia (mm)

(4) Total cross Section area of core

(5) Effective cross Sectional area of

core

(6) Clamping arrangement

(i) Channel Size

(ii) Bolt size and No.

(iii) Tie Rods size and No.

(iv) Painting

(a) Channels

(b) Tie Rods

(c) Bolts

(7) Whether top yoke is cut

for LV connection.

(8) If yes, at 7 above, whether

Reinforcement is done.

(9) Size of Support Channels

provided for Core base and bottom yoke (Single piece of channels are only

acceptable) this will not be applicable for Amorphous core. For

Amorphous core, core clap with locking arrangement with tank base

cover will be provided.

(10) Thickness of insulation

provided between core base

and support channel.

(11) core length (leg center to

leg center)

(12) Window height

(13) Core height

(14) Core weight only

(without channels etc.)

(E) INSPECTION OF WINDING

(I) Winding material

(1) Material used for

(a) HV winding

(b) LV winding

(2) Grade of material for

(a) HV winding

(b) LV  winding

3) Test certificate of

manufacturer (enclose copy)

for winding material of:

(a) HV

(b) LV

(II) CONSTRUCTIONAL DETAILS

(1) Size of Cross Sectional

area of conductor for :

(a) HV winding

(b) LV winding

(2) Type of insulation for

conductor of :

a) HV winding

(b) LV winding

(3) Diameter of wire used for

delta formation (mm)

(4) Diameter of coils in:

a) LV winding

i) Internal dia (mm)

ii) Outer dia (mm)

b) HV winding

i) Internal dia (mm)

ii) Outer dia (mm)

(5) Current Density of winding

material used for :

(a) HV

(b) LV

(6) Whether neutral formation on top.

(7) HV Coils/ Phase

a) Number

b) Turns / coil

c) Total turns

(8) LV Coils/ Phase

a) Number

b) Turns / coil

c) Total turns

(9) Method of HV Coil Joints

(10) Total weight of coils of

a) LV winding (kg)

b) HV winding (kg)

(F) INSULATION MATERIALS :

(I) MATERIAL :

1) Craft paper

a) Make

b) Thickness (mm)

c) Test Certificate of

manufacturer (enclose copy).

2) Press Board

a) Make

b) Thickness (mm)

c) Test Certificate of

manufacturer (enclose copy).

3) Material used for top and

bottom yoke and insulation

(II) Type   and thickness of

material used : (mm)

a) Between core and LV

b) Spacers

c) Inter layer

d) Between HV and LV winding

e) Between phases

f) End insulation

(G) CLEARANCES : (mm)

(I) Related to core and

windings

1) LV to Core (Radial)

2) Between HV and LV

(Radial)

3) (i)   Phase to phase

between HV Conductor

(ii) Whether two Nos. Press

Board each of minimum

1 mm thick provided to

cover the tie rods.

4) Thickness of locking spacers

between LV coils (mm)

5) Axial wedges between HV

and LV coils / phase (Nos.)

6) No. of radial spacers per

phase between HV coils

7) Size of duct between LV

and HV winding (mm)

(II) Between core - coil assembly

and tank : (mm)

1) Between winding and body:

a) Tank lengthwise

b) Tank Breadth wise

2) Clearance between top cover

and top yoke upto 100 kVA

and between top cover and top

most live part of tap changing

switch for 200 kVA and

above.

(H) TANK :

(I) Constructional details :

1) Rectangular shape

2) Thickness of side wall (mm)

3) Thickness of top and bottom

plate (mm)

4) Provision of slopping top cover

towards HV bushing.

Sl. Particulars As offered  As observed Deviation and

No Remarks

5) Tank internal dimensions (mm)

a) Length

b) Breadth

c) Height

(i) On LV side

(ii) On LV side

(II) General details :

1) Inside  painted  by  varnish/  oil

corrosion resistant paint (please

specify  which  type  of  coating

done).

2) Gasket between top cover and tank

i) Material

ii) Thickness (mm)

iii) Jointing over laps (mm)

3). Reinforcement of welded angle (specify

size and No. of angle provided ) on

side walls of tank.

4) Provision of lifting lugs:

a) Numbers

b) Whether lugs of 8 mm thick

MS Plate provided

c) Whether reinforced by welded

plates edge wise below the lug

upto re- enforcing angle of the

tank done.

5) Pulling lug of MS Plate

a) Nos.

b) Thickness (mm)

c) Whether provided on breadth

side or length side

6) Provision of air release plug

7) Provision of galvanized GI Nuts Bolts

with 1 No. Plain and 1 No. spring

washer.

8) Deformation of length wise side wall of

tank when subject to:

a) Vacuum of (-) 0.7 kg/sq cm for

30 minutes.

Sl.Particulars As offered As observed Deviation and

No Remarks

b) Pressure of 0.8 kg/sq

cm for 30 minutes.

(I) RAIDATORS :

1. Fin Radiators of 1.25 mm thick

sheet

a) Dimension of each fin

(LxBxT)

b) Fins per radiator

c) Total No. of radiators

2. Verification of manufacturer’s

test certificate regarding

Heat dissipation (excluding

Top and Bottom) in w/sq m

3. Verification of position of radiator

with respect to bushing.

(J) CONSERVATOR :

1. Dimensions ( L x D) (in mm)

3

2. Volume (m )

3. Inside dia of Conservator

tank pipe (mm)

4. Whether conservator outlet pipe is

projected approx. 20 mm inside the

conservator tank.

5. Whether arrangement made so

that oil does not fall on the

active parts.

6. Whether die cast metal oil level

gauge indicator having three

o o

positions at ( - 5 C, 30 C and

o

98 C) is provided .

7. Whether drain plug and filling

hole with cover is provided.

8. Inner side of the conservator Tank

painted with-

(K) BREATHER :

1. Whether    Die cast Aluminium

body breather for silica gel

provided.

2. Make

3. Capacity

Deviation and

Sl. No Particulars As offered As observed Remarks

(L) TERMINALS :

1. Material whether of Brass

Rods/ Tinned Copper.

a) HV

b) LV

2. Size (dia in mm)

a) HV

b) LV

3. Method of Star connection

formed on LV side of 6mm thick

(Should use Al./Cu. Flat bolted/

brazed with crimped lugs on

winding alternatively for 63 and

100 kVA ratings brazing is done

covered with tubular sleeve duly

crimped).

- Please state dimensions of Al/

Cu flat or tubular sleeve used. (mm)

4. Method of Connection of LV

winding to LV Bushing (end of

winding should be crimped with

lugs (Al/Cu) and bolted with

bushing stud).

5. Method of Connection of HV

winding to HV bushing (Copper

joint should be done by using

silver brazing alloy and for

Aluminium, brazing rod or with

tubular connector crimped at

three spots).

6. Whether SRB Ptube/insulated

paper used for formation of

Delta on HV.

7. Whether Empire sleeves used

on the portion of HV winding

joining to HV bushing.

8. Whether neutral formation is

covered with cotton tape

(M) BUSHINGS :

1. Whether HV bushings mounted

on side walls.

Whether sheet metal

2. pocket

used for mounting bushing

(pipe are not acceptable)

a) H V

b) L V

Whether arrangement for studs for fitting of

HV Bushing are in diamond shape (so

3. that Arcing Horns are placed vertically).

4. Position of mounting of LV bushings.

5. Bushing Clearance: (mm)

a) LV to Earth

b) HV to Earth

c) Between LV Bushings

d) Between HV Bushings

(N) TANK BASE CHANNEL

/ ROLLERS :

1. Size of channel (mm)

2. Whether channels welded across the length of

the tank

3. Size and type of roller (mm)

(O) OIL :

1. Name of supplier

2. Break down voltage of oil: (kV)

i) Filled in tanked transformer

ii) In storage tank (to be tested by Inspecting

Officer).

3. Supplier’s test certificate(enclose copy)

(P) ENGRAVING :

1. Engraving of Sl. No. and name of firm.

i) On bottom of clamping channel of core-coil

assembly.

ii) On side wall and top cover of tank along

with date of despatch.

i) MS plate of size 125x125 mm welded on

(Q) width side of stiffner

ii) Following details engraved (as per

approved GTP):

(a) Serial Number

(b) Name of firm

(c) Order No. and Date

(d) Rating

(e) Name of Inspecting Officer

(f) Designation

(g) Date of dispatch

(R) NAME PLATE DETAILS :

Whether Name Plate is as per approved

drawing

(S) Colour of Transformer

1. Tank body colour shell be as per

annexure -paint which is attach here with

2. Conservator colour shell be as per annexure

- paint which is attach here with

(T) CHECKING OF TESTING FACILITIES:

TESTS :

1. No Load Current

2. No Load Loss

3. % Impedance

4. Load Losses

5. Insulation Resistance Test

6. Vector Group Test (phase relationship)

7. Ratio and Polarity test relationship

8. Transformer Oil Test (Break Down Voltage)

9. Magnetic Balance

10. Measurement of winding resistance (HV

and LV both)

11. Induced over voltage withstand test

(Double voltage and Double frequency)

12. Separate source power frequency withstand

test at 28 kV for HV and 3 kV for LV (one

minute).

13. Air pressure/ Oil leakage Test

14. Vacuum test

15. Unbalanced current test

16. Temperature rise (Heat Run) test.

We have specifically checked the following and

found the same as per G.T.P./deviations

(U) observed as mentioned against each:

i) Rustlessness of CRGO laminations used

ii) Core steps

iii) Core area

iv) Core weight

v) Winding cross sectional area

a) LV

b) HV

vi) Weight of windings

vii) Clearance between winding and wall of

tank (mm)

a) Length-wise

b) Breadth-wise

viii) Clearance between top of yoke/ top most live

part of tap changer to tank cover.

ix) Details of Neutral formation

x) Connections to bushings:

a) LV

b) HV

xi) Slope of tank top

xii) Position of mounting of bushings

Annexure-A

Check-list for Inspection of prime quality CRGO for Transformers

During inspection of PRIME CRGO, the following points needs to be checked by the Transformer

manufacturer. Utility’s inspection shall verify all these points during inspection:-

A) In case PRIME cutting is at works of Transformer Manufacturer:

1 Review of documents:

Purchase Order (unpriced) to PRIME CRGO supplier/ Authorized Agency 

Manufacturer’s test certificate 

Invoice of the Supplier 

Packing list 

Bill of Lading 

Bill of Entry Certificate by Customs Deptt. 

Reconciliation Statement as per format below 

Certificate of Origin 

BIS Certificate 

Format for Reconciliation/Traceability records

Packing List No. / Date /Quantity of PRIME CRGO received

Name of Manufacturer

Manufacturer test certificate No. / date

Serial Details of Drawing Quantity Cumulative Balance in

No. Package/Job Reference involved Quantity Stock

Consumed

2.1 Inspection of PRIME CRGO Coils:

a) PRIME CRGO-Manufacturer’s identification Slip on PRIME CRGO Coils

b) Visual Inspection of PRIME CRGO Coils offered as per packing list (for

verification of coil details as per Test certificate & healthiness of packaging).

c) Unique numbering inside of each sample of PRIME CRGO coil and verification

of records to be maintained in the register for consumption of CRGO coil.

d) ISI logo Sticker on packed mother coil and ISI logo in Material TC.

2.2 During inspection of PRIME CRGO, surveillance testing of sample shall be carried out for

Stacking Factor, Permeability, Specific watt loss at 1.5 Tesla and/or 1.7 Tesla depending on

the grade of PRIME CRGO and aging test etc. applicable as per relevant IS/ IEC

standard, Tech. Spec., MQP and Transformer manufacturer plant standard.

Inspection Clearance Report Would Be issued after this inspection

3 Inspection of PRIME CRGO laminations: Transformer manufacturer will maintain

records for traceability of lamination to PRIME CRGO coils and burr/bow on lamination

shall be measured.

4. Inspection at the time of core building:

Visual Inspection of PRIME CRGO lamination. In case of suspected mix-up/ rusting/

decoloration,Samples may be taken for testing on surveillance basis mentioned in

A.2.2 above.

Above tests shall be witnessed by utility. In case testing facilities are not available at

Manufacturer‘s work, the sample(s) sealed by utility to be sent to approved labs for testing.

Inspection Clearance Report would be issued after this inspection

B) In case PRIME CRGO cutting is at Sub-vendor of Transformer Manufacturer:

1 Review of documents:

Purchase Order (unpriced) to PRIME CRGO supplier/ Authorized Agency 

Purchase Order (unpriced) to Core Cutter 

Manufacturer test certificate 

Invoice of the Supplier 

Packing List 

Bill of Lading 

Bill Of Entry Certificate by Customs Deptt. 

Reconciliation Statement as per format below 

Certificate of Origin 

BIS Certificate 

Format for Traceability records as below:-

Packing List No./date/quantity of PRIME CRGO received

Name of Manufacturer

Manufacturer test certificate No. / date

Serial Name Of Details of Drawing Quantity Cumulative Balance in Dispatch

No. Customer Package/Job Reference involved Quantity Stock Details

Consumed

2.1 Inspection of PRIME CRGO Coils:

a) PRIME CRGO-Manufacturer’s identification Slip on PRIME CRGO Coils

b) Visual Inspection of PRIME CRGO Coils offered as per packing list (for

verification of coil details as per Test certificate & healthiness of packaging).

c) Unique numbering inside of each sample of PRIME CRGO coil and verification

of records to be maintained in the register for consumption of CRGO coil.

d) ISI logo Sticker on packed mother coil and ISI logo in Material TC.

2.2 During inspection of PRIME CRGO, surveillance testing of sample shall be carried out for

Stacking Factor, Permeability, Specific watt loss at 1.5 Tesla, Thickness depending on the grade

of PRIME CRGO and aging test etc. applicable as per relevant IS/IEC standard,

Tech.Spec., MQP and Transformer manufacturer plant standard.

Inspection Clearance Report would be issued after this inspection

3 Inspection of PRIME CRGO laminations:

Transformer manufacturer representative will inspect laminations and issue their internal

Inspection Clearance Report. Inspection will comprise of review of traceability to prime

CRGO coils, visual Inspection of PRIME CRGO laminations and record of burr/bow. After

clearance given by the transformer manufacturer, utility will issue an Inspection

Clearance Report after record review. If so desired by Utility, their representative may

also join transformer manufacturer representative during this inspection.

Inspection Clearance Report would be issued after this inspection

4 Inspection at the time of core building

Visual inspection of PRIME CRGO laminations. In case of suspected mix-

up/rusting/decoloration, samples may be taken for testing on surveillance basis for

tests mentioned in B.2.2.

Inspection Clearance Report would be issued after this inspection

NOTE:-

a) Transformer Manufacturer to ensure that PRIME CRGO is procured from

POWERGRID approved vendors and CRGO manufacturer should have valid

BIS Certificate for respective offered Grade.

b) Transformer Manufacturer should also involve themselves for ensuring the quality of

CRGO laminations at their Core Cutter’s works. They should visit the works of their

Core cutter and carry out necessary checks.

C) General

If a surveillance sample is drawn and sent to TPL ( if testing facility not available

with the manufacturer), the transformer manufacturer can continue manufacturing

at their own risk and cost pending TPL test report on PRIME CRGO sample

drawn. Decision for acceptance of PRIME CRGO shall be based upon report of

sample drawn.

These checks shall be read in –conjunction with approved quality

plan, specification as a whole and conditions of contract.

Sampling Plan (PRIME CRGO)

33/11 kV -1st transformer and subsequently at random 10% of

Transformers (min.1) offered for inspection.

DTs and other ratings -1st transformer and subsequently at random 10% of

Transformers (min.1) offered for inspection.

NOTE:- One sample for each lot of CRGO shall be drawn on surveillance basis.

CRGO has to be procured only from POWERGRID approved vendors. List of such vendors

is available at the following website. Since the list is dynamic in nature, the site may be

checked from time to time to see the list of approved vendors.

http://apps.powergridindia.com/ims/ComponentList/Power-

former%20upto%20420%20kV-CM%20List.pdf

SL. NO ITEM VENDOR NAME

1 CRGO STEEL M/S NIPPON STEEL & SUMITOMO METAL CORP, JAPAN

CRGO STEEL M/S KAWASAKI CORPORATION/JFE,JAPAN

CRGO STEEL M/S A.K.STEEL, USA

CRGO STEEL M/S POSCO KOREA

CRGO STEEL M/S AST ITALY

CRGO STEEL M/S TKES GERMANY

CRGO STEEL M/S UGINE DIVISION DUSINOR SACLAR, S.A., FRANCE

CRGO STEEL M/S ORB ELECTRICALS STEELS, UK

CRGO STEEL M/S PREUSSAG HANDEL, GERMANY

CRGO STEEL M/S ACESITA, BRAZIL

CRGO STEEL M/S VIZ STEEL, RUSSIA valid upto 05.02.2018

CRGO STEEL WITH M/S TKES INDIA PVT. LTD. NASIK, (approval valid upto 20.08.2016)

FINAL PROCESS OF and subject to condition

COATING & ANNEALING

OF OF SEMIPROCESSED

CRGO MOTHER COIL

(SOURCED FROM TKES,

GERMA