BROAD SPECIFICATION

FOR SUBSEA OPTICAL FIBRE CABLE

The optical fibre cable shall have high strength, low loss and should be designed to meet both mechanical, optical requirement and shall be suitable for laying up to 100 meters of water depth. The optical fibre cable shall consist of 24 nos. single mode fibres, complying with ITU- T-G-652.D suitable for working in the applicable wavelength region. Number of fibres of each kind and their construction shall be selected so as not to load the individual fibres beyond 50% of their bandwidth capacity and 50% of the number of each fibre shall be available spare in the cable for future use.

Contractor and subsea Cable vendor shall ensure the compatibility of subsea cable optical fibres and the optical convertors for signal propagation.

Splicing and preparation of optical fibres for termination shall be done with standard and approved / certified equipment. All optical fibre cores coming shall be first terminated at fibre termination cabinet. Terminals and adapters used shall conform to the relevant specifications. Patch cable/extension cable from splitter JB (first terminal box) to the terminal equipment (PLC cabinet/DCS  cabinet/etc)  shall  be  redundant,  routed  separately  and  adequately  protected against physical damage. Each fibre within the cable shall be uniquely coloured for identification.

Optical equipment  for end-to-end  communication  shall be provided  in redundant  fashion. These shall be part of the PLC/Control system for communicating the ‘tags’/’parameters’ from

unmanned platforms to the main /process platform and also achieve control from main platform as described in the basic bid work. These systems shall be scalable and modular. Suitable Fibre optic interface modules/communication modules, standard connectors, switches, network components and  cross  connect  as  required  per  scope  of  work  and  specification  shall  be provided for effective connectivity.

As a minimum, the offered sub-sea optical fibre cables and associated accessories shall be designed, manufactured, tested, supplied and installed in accordance with the applicable provisions of the latest revision of relevant National/International Codes, Standards & Regulations listed below. In the event of a conflict between various Codes and Standards, the one which is most stringent, shall be applicable.

IEC 60794                   Optical Fibre Cable

IEC 60793-2               Optical fibres - Part 2: Product specifications - General.

IEC 60794-1-1            Optical fibre cables - Part 1-1: Generic specification - General

IEC 60794-1-2 	Optical fibre cables - Part 1-2: Generic specification - Cross reference table for optical cable test procedure

ITU-T Recommendations

G.971                          General features of optical fibre submarine cable systems

G.972                          Definition of terms relevant to optical fibre submarine cable systems

G.973 	Recommendation that  covers  the  interface  requirements  and  system performance of repeaterless optical fiber submarine cables

G.976                          Test methods applicable to optical fibre submarine cable systems

G.978                          Characteristics of optical fibre submarine cables

G.652.D                       Characteristics of a single-mode optical fibre and cable

The sub-sea optical fibre cable shall be manufactured, supplied and laid in a single length without field joints. The vendor shall also provide details of the maximum allowable tension during laying and pulling operations. The vendor shall be responsible for ensuring that all the offered cables and accessories are suitable for the operating/site conditions specified in the bid package. The contractor shall ensure presence of cable manufacturer’s representative on laying barge/ vessel during offshore installation and commissioning.